## Sheet1
PANIPOKHARI MODBUS ADDRESS INLET PANEL |  | KHUMALTAR MODBUS ADDRESS INLET PANEL
CHAMBER -B BALL VALVE POSITION |  | CHAMBER -C1 BALL VALVE POSITION
DATA REGISTER | D460 | DATA REGISTER | D330
MODBUS ADDRESS | 400461 | MODBUS ADDRESS | 400331
CHAMBER -C1 BALL VALVE POSITION |  | CHAMBER -C2 BALL VALVE POSITION
DATA REGISTER | D470 | DATA REGISTER | D340
MODBUS ADDRESS | 400471 | MODBUS ADDRESS | 400341
CHAMBER -C2 BALL VALVE POSITION |  | CHAMBER -D BALL VALVE POSITION
DATA REGISTER | D480 | DATA REGISTER | D360
MODBUS ADDRESS | 400481 | MODBUS ADDRESS | 400361
WATER TANK -1 LEVEL |  | CHAMBER -E BALL VALVE POSITION
DATA REGISTER | D280 | DATA REGISTER | D370
MODBUS ADDRESS | 400281 | MODBUS ADDRESS | 400371
WATER TANK-2 LEVEL |  | SRT-1A WATER TANK LEVEL
DATA REGISTER | D300 | DATA REGISTER | D220
MODBUS ADDRESS | 400301 | MODBUS ADDRESS | 400221
INLET FLOW METER |  | SRT-1B WATER TANK LEVEL
DATA REGISTER | D320 | DATA REGISTER | D240
MODBUS ADDRESS | 400321 | MODBUS ADDRESS | 400241
INLET FLOW METER |  | SRT-2A WATER TANK LEVEL
DATA REGISTER | D340 | DATA REGISTER | D260
MODBUS ADDRESS | 400341 | MODBUS ADDRESS | 400261
SRT-2B WATER TANK LEVEL
|  | DATA REGISTER | D280
|  | MODBUS ADDRESS | 400281
SRT-1A INLET FLOW METER
|  | DATA REGISTER | D340
|  | MODBUS ADDRESS | 400341
SRT-1B INLET FLOW METER
|  | DATA REGISTER | D360
|  | MODBUS ADDRESS | 400361
SRT-2A INLET FLOW METER
|  | DATA REGISTER | D300
|  | MODBUS ADDRESS | 400301
SRT-2B INLET FLOW METER
|  | DATA REGISTER | D320
|  | MODBUS ADDRESS | 400321

## Sheet2
PANIPOKHARI PLC MODBUS RTU COMMAND
TANK-1 A | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D270 | D280 | 400271 USED ADDRESS
TX :-01 03 01 0E 00 A4 34
TANK-2 B | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D290 | D300 | 400291 USED ADDRESS
TX :-01 03 01 22 00 02 65 FD
INLET CH-B | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D310 | D340 | 400311 USED ADDRESS
TX :-01 03 01 36 00 02 25 F9
INLET CH-C | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D330 | D320 | 400311 USED ADDRESS
TX :-01 03 01 4A 00 02 E4 21
KHUMALTAR PLC MODBUS RTU COMMAND
SRT-1 TANK-A | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D210 | D220 | 400211 USED ADDRESS
TX :-01 03 00 D2 00 01 24 33
SRT-1 TANK-B | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D230 | D240 | 400231 USED ADDRESS
TX :-01 03 00 E6 00 01 65 FD
SRT-2 TANK-A | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D250 | D260 | 400251 USED ADDRESS
TX :-01 03 00 FA 00 01 A4 3B
SRT-2 TANK-B | DATA REGISTER |  | PLC MODBUS ADDRESS
LEVEL SENSOR | D270 | D280 | 400271 USED ADDRESS
TX :-01 03 01 0E 00 01 E4 35
SRT-1 EFM -D | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D330 | D340 | 400331 USED ADDRESS
TX :-01 03 01 4A 00 01 A4 20
SRT-1 EFM -E | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D350 | D360 | 400351 USED ADDRESS
TX :-01 03 01 5E 00 01 E4 24
SRT-2 EFM C-1 | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D290 | D300 | 400291 USED ADDRESS
TX :-01 03 01 22 00 01 25 FC
SRT-2 EFM C-2 | DATA REGISTER |  | PLC MODBUS ADDRESS
FLOWMETER | D310 | D320 | 400311 USED ADDRESS
TX :-01 03 01 36 00 01 65 F8